# Configuration & Commissioning Manual
Omron E2E-NEXT Series IO-Link Proximity Sensor (E2E-X16MB1T12)

# 1. System Overview

This manual outlines the configuration, data mapping, and commissioning process for the Omron E2E-X16MB1T12 proximity sensor operating in IO-Link mode. The guide is structured to assist in integrating smart sensors into industrial automation training systems, providing clear documentation suitable for BTEC and Higher National engineering modules.

# 2. TIA Portal Hardware Configuration

When assigning the sensor to an IO-Link master (e.g., AL1350 or AL1300) in Siemens TIA Portal, the correct submodule must be selected to match the sensor's Process Data (PD) size.

Navigate to the hardware catalog for the configured IO-Link Master.

Expand the IO-Link Input + PQI folder.

Select the submodule: IO-Link In 2 Byte + PQI (This matches the 2-byte specification in the Omron IODD file).

Assign the port to an available I-address block (e.g., %IB3...%IB5).

# 3. Process Data (Cyclic) Mapping

The E2E-NEXT series transmits 2 bytes of process data. Siemens natively handles Big-Endian byte ordering, meaning the high byte (Monitor Output) arrives first. The data maps sequentially into the reserved input address block.

| Address / Bit | Data Type | Signal Description |
| --- | --- | --- |
| Byte 0 (e.g., %IB3) | USInt (8-bit) | Monitor Output (Raw detection distance 0-255) |
| Byte 1, Bit 0 (e.g., %I4.0) | Bool | Switching State (Main NO/NC target detection) |
| Byte 1, Bit 4 (e.g., %I4.4) | Bool | Instability Detection (Target on edge of range) |
| Byte 1, Bit 5 (e.g., %I4.5) | Bool | Excessive Proximity (Target dangerously close) |
| Byte 2 (e.g., %IB5) | Byte | PQI (Port Quality Info) from IO-Link Master |

# 4. PLC Data Type (UDT) Implementation

To ensure clean integration with SCL or Ladder logic, a custom UDT should be created. This unpacks the raw byte data into strictly typed, named variables.

TYPE "Omron_E2E_IOLink"
STRUCT
   Monitor_Output      : USInt;
   Switching_State     : Bool;
   Spare_1             : Bool;
   Spare_2             : Bool;
   Spare_3             : Bool;
   Instability_Warning : Bool;
   Excessive_Proximity : Bool;
   Spare_4             : Bool;
   Spare_5             : Bool;
END_STRUCT;
END_TYPE

Once created, apply this UDT to the first input byte of the port (e.g., %I3.0) in the PLC Tags table.

# 5. Parameterization (Acyclic Data)

Unlike standard digital inputs, IO-Link sensors allow parameters (such as the detection threshold or NO/NC logic) to be changed remotely via Acyclic Data.

Static Commissioning: Use the Siemens S7-PCT (Port Configuration Tool) plugin. Import the Omron IODD XML file, select the port, and manually adjust the switchpoint via the graphical interface.

Dynamic Adjustment: Use the IO_LINK_DEVICE standard function block in TIA Portal to write to the sensor's parameter indexes (ISDU). This allows operators to change sensor ranges dynamically from a WinCC Unified HMI screen.